ELECTRICAL PANELBOARD AND SWITCHBOARD IDENTIFICATION STANDARDS

All electrical panelboard, switchboard identification must follow the conventions given below:

Panelboard and Switchboard Schedules and Directories:

- All new schedules shall use the format given in the sample on the following page.

- All areas in Red are to be filled in, corrected or verified completely anytime a panelboard or switchboard is installed, changed, or updated for any reason.

- Each space in the schedule should have a completed load description. If it is a spare breaker or an unused space label it as such.

- An editable digital copy of the panelboard schedule, created in Microsoft Word, is to be included in Project Closeout Documents when complete.

- For panelboards with more than 42 poles, create a second sheet with properly numbered circuits

- For the Schedule Circuit Number, the Schedule CKT Number must match the numbering system used on the breakers.

- See Schedule and Directory Legend below for guidance on completing individual sections of the schedule.

Schedule and Directory Legend

- Panelboard/Switchboard Schedule: Modify to indicate which type the schedule will be describing.

- Panel: Insert panelboard or switchboard name

- Voltage/Ph: Insert voltage and phase (480Y/277V/3ph, 208Y/120V/3ph or 240/120/1ph)

- MAINS: Insert panelboard main bus ampere rating as shown on manufacturers nameplate

- MAIN CKT BKR: Insert main circuit breaker ampere rating or if no main circuit breaker, insert MLO for Main Lugs Only

- AIC: Insert the Amperes Interrupting Capacity for which the panelboard is designed for The Panelboard Utilization Voltage Rating.

- Location: Insert four-digit Building Number followed by the Building Name

- Room #:  Insert Room number where panelboard is located

- Date: Insert date Panelboard schedule information is completed or revised

- Contractor: Insert name of contractor or responsible party who gathered information for panelboard schedule

- Phone #: Insert above contractor or responsible party’s primary business phone number. Do not include direct cellular numbers for company or University representatives.

- Panelboard Fed From: Insert Source Panelboard Name and Circuit Number Feeding The Panelboard.

- Feeding Panel Room #: Insert Room Number where Source Panelboard is located.

- Short Circuit Current: If the panelboard or switchboard is the service entrance rated board for the facility, include the short circuit amperes available at the service entrance board. Otherwise insert N/A.

- AMPS/#Poles: Insert circuit breaker ampere trip rating and number of poles, 1, 2, or 3.

- LOAD: Insert load description and room number where load is located.

Sample Schedule

| PANELBOARD/SWITCHBOARD SCHEDULE |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Panel: XXXXX |  |  | Location: #### XXXXXX |  |  |
| Voltage/Ph: ###/###/#PH |  |  | Room #: #### |  |  |
| MAINS: ###A |  |  | Date: ####/##/#### |  |  |
| MAIN CKT BKR: XXXXXXXXXXXX |  |  | Contractor: XXXXXXX |  |  |
| AIC: ####A |  |  | Phone #: ###-###-#### |  |  |
| Panel Fed From: XXXXXXXXX |  |  | Feeding Panel Room #: #### |  |  |
| Short Circuit Current (for Svc Ent. Rated Only): ####A |  |  |  |  |  |
| Ckt | Amps/ #Poles | Load | Ckt | Amps/ #Poles | Load |
| 1 | xxA/xP | Circuit/Load Description | 2 | xxA/xP | Circuit/Load Description |
| 3 | xxA/xP | Circuit/Load Description | 4 | xxA/xP | Circuit/Load Description |
| 5 | xxA/xP | Circuit/Load Description | 6 | xxA/xP | Circuit/Load Description |
| 7 | xxA/xP | Circuit/Load Description | 8 | xxA/xP | Circuit/Load Description |
| 9 | xxA/xP | Circuit/Load Description | 10 | xxA/xP | Circuit/Load Description |
| 11 | xxA/xP | Circuit/Load Description | 12 | xxA/xP | Circuit/Load Description |
| 13 | xxA/xP | Circuit/Load Description | 14 | xxA/xP | Circuit/Load Description |
| 15 | xxA/xP | Circuit/Load Description | 16 | xxA/xP | Circuit/Load Description |
| 17 | xxA/xP | Circuit/Load Description | 18 | xxA/xP | Circuit/Load Description |
| 19 | xxA/xP | Circuit/Load Description | 20 | xxA/xP | Circuit/Load Description |
| 21 | xxA/xP | Circuit/Load Description | 22 | xxA/xP | Circuit/Load Description |
| 23 | xxA/xP | SPARE BREAKER | 24 | xxA/xP | SPARE BREAKER |
| 25 | xxA/xP | SPARE BREAKER | 26 | xxA/xP | SPARE BREAKER |
| 27 | xxA/xP | SPARE BREAKER | 28 | xxA/xP | SPARE BREAKER |
| 29 | xxA/xP | SPARE BREAKER | 30 | xxA/xP | SPARE BREAKER |
| 31 | xxA/xP | SPARE BREAKER | 32 | xxA/xP | SPARE BREAKER |
| 33 | xxA/xP | Unused Space | 34 | xxA/xP | Unused Space |
| 35 | xxA/xP | Unused Space | 36 | xxA/xP | Unused Space |
| 37 | xxA/xP | Unused Space | 38 | xxA/xP | Unused Space |
| 39 | xxA/xP | Unused Space | 40 | xxA/xP | Unused Space |
| 41 | xxA/xP | Unused Space | 42 | xxA/xP | Unused Space |

Panelboard and Switchboards Nameplate:

All panelboards and switchboards shall be identified with a permanent nameplate meeting the following criteria:

- Material and Thickness: Engraved, Laminated acrylic or melamine nameplate, 1/16 inch thick, and having predrilled holes for attachment hardware if needed

- Letter Color: White.

- Background Color: Black except for the Emergency Panelboard, which are to have a red background

- Maximum Temperature: Able to withstand temperatures up to 160 deg F.

- Minimum Label Size: Length and width vary for required label content

- Minimum Letter Size: 1/4 inch height for Electrical Panelboards and Disconnect Switches. 3/8 inch height for Main Switchboards (SWBD) and Switchgear (SWGR).

- Fasteners: Stainless-steel rivets or machine screws not to exceed 1/8” beyond surface to which nameplate is mounted or create and sharp edges inside the panelboard, or double-face adhesive.

- Adhesive: Contact-type permanent adhesive, compatible with nameplate label and with substrate.

- All labels shall follow one of the examples given below as applicable to the panel type and all Areas in Red are to be complete, correct and verified completely anytime a panel is installed, changed, or updated for any reason.

Example Panelboard Label

Panel: XXXX

Voltage:###Y/###V, #PH

FED FROM: Panel XXXX,

Example Emergency Panelboard Label

EMERGENCY

Panel: XXXX

Voltage:###Y/###V, #PH

FED FROM: Panel XXXX,

Example Switchboard Label

Switchboard ID: XXXXX

Voltage: ###Y/### V, #PH

FED FROM: XXXX

Install Date: MM/DD/YYYY